**\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_**

**ARCHITECTURE, ENGINEERING AND CONSTRUCTION**



ARCHITECTURE & ENGINEERING

326 East Hoover, Mail Stop B

Ann Arbor, MI 48109-1002

Phone: 734-764-3414

Fax: 734-936-3334

BuildingName  
The Description of the Project  
P00000000 0000

DOCUMENTS

SPECIFICATION DIVISION 23

NUMBER SECTION DESCRIPTION

DIVISION 23 HEATING, VENTILATING AND AIR CONDITIONING (HVAC)

SECTION 238221 - BLOWER COIL UNITS

END OF CONTENTS TABLE

ction: June 2011.

Blower coils for the purposes of this specification are units of GREATER than 1/2 HP (and therefore normally have three phase motors) usually with belt drive fans. Blower coils typically provide higher air flows and fan static pressures than are AVAILABLE from fan coil units, in a compact package. Upper CFM limit for standard units is TYPICALLY 3000-4000 cfm.

Blower coils are available in numerous CONFIGURATIONS and with multiple options; this SPECIFICATION is therefore NECESSARILY outline in nature. edit section carefully to make it project specific. Specifications for mfr. provided CONTROLS, factory piping packages, DX coils, cabinets for finished space use, and INTEGRAL grilles/registers/DIFFUSERS are not included, and must be added if required. U-M specification 238219 "Floor Mounted Fan Coil units Unducted" is a good resource for control spec.s and other spec. language which may be useful when specifying blower coil units.

1. DIVISION 23 HEATING, VENTILATING AND AIR CONDITIONING (HVAC)
   1. SECTION 238221 - BLOWER COIL UNITS
      1. General
         1. RELATED DOCUMENTS

INCLUDE PARAGRAPH 1.1.A and b IN EVERY SPECIFICATION SECTION. EDIT related sections 1.1.B to make it project specific.

* + - * 1. Drawings and general provisions of the Contract, Standard General and Supplementary General Conditions, Division 1 Specification Sections, and other applicable Specification Sections including the Related Sections listed below, apply to this Section.

CAREFULLY VERIFY, EDIT AND COORDINATE RELATED SECTIONS.

* + - * 1. Related Sections:

Section 220513: Motors.

Section 220719: Mechanical Systems Insulation.

Division 26: Electrical.

* + - 1. SUMMARY
         1. Section Includes:

Horizontal and vertical blower coil units with motors 1/2 HP and greater, and hydronic coils.

* + - 1. COORDINATION
         1. Coordinate dimensions and arrangement of blower coils with building elements including to maintain all maintenance clearances. Pay special attention to required electrical clearance.
      2. submittalS
         1. Submit the following product data for approval:

Heating and cooling coil total and sensible heat transfer capacity, entering and leaving water temperatures, water flow rate, water pressure drop, and air pressure drop.

Piping connections including size, material types, and dimensioned locations for each service.

Ductwork connections including sizes, locations, and methods of connections to mating ductwork.

Locations of electric power connections.

Details of equipment assemblies indicating dimensions, weights, required clearances, component locations, and location and size of each field connection. Include cabinet construction details: panel gauge, removal method for access panel, cabinet mounting method, and filter and fan motor removal method.

Details of motor including type, manufacturer and electrical characteristics.

Octave band and A-weighted sound power data for each unit type at fan coil rated capacity, tested per AHRI Standard 350.

Evidence of UL or ETL listing and labeling.

Unhide the below hidden text if disconnect switch, controls, transformer, or 3 speed fan relay board are to be provided by the fan coil mfr.

Wiring Diagrams: Power, disconnect switch, controls, transformer and three-speed fan control relays.

Control transformer-sizing calculations.

Detailed information on fan control relay board.

* + - * 1. Equipment schedule with the following information for each unit type:

Equipment tag.

Room number of thermostat location.

Model number.

Manufacturer’s size designation.

Configuration (2-pipe or 4-pipe).

Number of coils, number of rows per coil, fin spacing for each coil.

Heating and cooling capacity.

Airflow rate and motor watts at each fan speed.

* + - * 1. Maintenance schedules and repair part numbers and manufacturer of motors, coils, integral controls, relay board, control transformer, and air filters.
      1. DELIVERY, STORAGE AND HANDLING
         1. Mark each blower coil cabinet with the room number where it is scheduled to be installed.
         2. Mark each blower coil shipping box with the room number where it is scheduled to be installed.
         3. Support piping to prevent damage to pipe and coil headers during shipping.
         4. Restrain fans and other components to prevent damage during shipping.
         5. Shipping protection shall be provided by Manufacturer to insure that the interior and exterior of each unit is completely protected from dirt or weather. Duct and pipe openings must be covered with sealed sheet metal, plastic or other durable means to ensure unit cleanliness is maintained.
      2. QUALITY ASSURANCE
         1. Manufacturers and Products: The products and manufacturers specified in this Section establish the standard of quality for the Work. Subject to compliance with all requirements, provide specified products from the manufacturers named in Part 2.
         2. Reference Standards: Products in this section shall be built, tested, and installed in compliance with the specified quality assurance standards; latest editions, unless noted otherwise.

ANSI/AHRI 350 Sound Rating of Non-Ducted Indoor Air-Conditioning Equipment.

ANSI/AHRI Standard 440: Performance Rating of Room Fan-Coils.

NFPA 70- National Electric Code.

NFPA 90A Installation of Air-Conditioning and Ventilating Systems.

ANSI/ASHRAE 62.1 Section 5 (Systems and Equipment) and Section 7 (Construction and Start-up).

ANSI/ASHRAE 90.1-2007 Energy Standards for Low Rise Buildings Except Low Rise Residential Buildings.

ASTM C916 - Standard Specification for Adhesives for Duct Thermal Insulation.

ASTM C411 Standard Test Method for Hot-Surface Performance of High-Temperature Thermal Insulation

ASTM C612 Standard Specification for Mineral Fiber Block and Board Thermal Insulation.

ASTM E84 Standard Test Method for Surface Burning Characteristics of Building Materials

ASTM A653 Standard Specification for Steel Sheet, Zinc-Coated (Galvanized) or Zinc-Iron Alloy-Coated (Galvannealed) by the Hot-Dip Process

Units shall be Underwriters Laboratories (UL) or Intertek (ETL) listed.

* + - 1. warranty
         1. Provide a complete parts and labor warranty for a minimum of one year from the date of Substantial Completion.
    1. PRODUCTS
       1. MANUFACTURERS
          1. Acceptable Manufacturers:

Airtherm.

Enviro-Tec by Johnson Controls.

International Environmental Corporation.

Daikin Applied.

Trane.

Verify the required project specific dimensions for the Blower coils and schedule or specify accordingly. Manufacturer's standard HEIGHT units may not fit properly in existing facilities.

LIST blower coil Sound power LEVELS in the blower coil schedule or in the SPECIFICATIONS. Be particularly cautious for blower coils used in sound sensitive areas.

This SPECIFICATION assumes none of the blower coil CONTROLS are provided by the blower coil mfr. if any controls are to be provided by the mfr. (disconnects, control transformer, etc.), edit this specification to include those requirements. U-M specification 238219 "Floor Mounted Fan Coil units Unducted" is a good resource for control spec.s which may be useful when specifying blower coil controls.

* + - 1. BLOWER COIL UNIT CONSTRUCTION
         1. Dimensions: Maximum allowable dimensions as indicated on the Drawings.
         2. Casing Construction:

Construction: Minimum 18 gauge, G60 galvanized or A40 galvannealed steel or as scheduled. Construct to eliminate racking.

Access panels shall be fully insulated and attached with fasteners on at least two opposite sides. No coil or drain piping or electrical connections shall pass through any access panel.

One inch duct collars if connected to ductwork.

* + - * 1. Insulation: Exterior panels and access panels: Foil faced minimum 1-inch-thick, 1-1/2 lb density fiberglass fire resistant insulation complying with the following:

ASTM C 411 Standard Test.

Attach with adhesive complying with ASTM C 916.

Fire-Hazard classification, insulation and adhesive combined: Maximum flame-spread index of 25 and smoke-developed index of 50 when tested according to ASTM E 84.

Airstream Surfaces: Surfaces in contact with the airstream shall comply with requirements in ASHRAE 62.1.

* + - 1. HYDRONIC COILS
         1. Hydronic Coils: Copper tube, minimum 0.025 inch wall thickness, with mechanically bonded aluminum fins, maximum of 12 fins per inch, copper headers and copper connections; rated for a minimum working pressure of 200 psig and a maximum entering-water temperature of 220 degrees F.

Factory test all coils as specified in the Source Quality Control article.

Include manual air vent and drain connections.

Chilled water and dual-temperature water coil casings, tracks, baffles, and supports shall be of stainless steel construction.

* + - 1. DRAIN PANS
         1. Condensate Drain Pan: Fabricate drain pans and drain connections to comply with ASHRAE 62.1.

Drain pan: Stainless steel, insulated.

Locate under cooling coil allowing the drain pan to be fully inspected and cleaned.

Slope to drain completely dry upon fan coil shutdown.

select below, one of the four code required methods of protecting against primary drain PAN failure and show drain termination points on the drawings. Delete the other three options.

Overflow drain pan connection: shall be on the same side and at a higher elevation than the primary drain pan connection.

Water-level detection device conforming to UL 508, factory wired to shut off the equipment prior to drain pan overflow. With auxiliary contact to simultaneously signal owner's Building Automation System.

Auxiliary drain pan with drain connection.

Auxiliary drain pan with capped or no drain connection, with a water-level detection device conforming to UL 508, factory wired to shut off the equipment prior to auxiliary drain pan overflow. With auxiliary contact to simultaneously signal owner's Building Automation System.

* + - 1. Filters
         1. Minimum arrestance according to ASHRAE 52.1, and a minimum efficiency reporting value (MERV) according to ASHRAE 52.2.

Disposable Type: 2 inch pleated cotton-polyester media: 90 percent arrestance and MERV A rating of 8 (or as scheduled) when tested per Appendix J of ASHRAE 52.2.

Select below, direction of FILTER removal. when selecting, Consider the obstructions to filter removal at the blower coil mounting LOCATION.

Provide filters that are removable horizontally from the casing.

Provide filters that are removable vertically from the casing.

If mixing dampers are required, INDICATE such on the CONTRACT drawings.

* + - 1. inlet damper mixing section
         1. Provide when indicated on Drawings.
         2. The outside and return airstreams shall be directed into each other in a mixing box by parallel blade damper assemblies oriented to facilitate mixing of the airstreams.

Section shall be constructed of minimum 18 gauge galvanized steel.

Two, steel, low leak parallel blade dampers in a heavy-gauge steel frame with extruded vinyl blade seals and flexible metal jamb seals.

Provide extended drive rod for externally mounted actuator connection.

Provide access panels for access to the section's internal components.

Indicate the fan type (fc, bi, inlet type, etc.)on the drawing schedules, or add below. FC is typical. If fan is direct drive, CONSIDER using the fan coil spec, OTHERWISE edit the below.

Below section will allow the blower coil mfr. to provide their standard QUALITY fans and drives. for projects with large QUANTITIES of blower coils, consider editing THE below to specify higher QUALITY fans and drives. U-M spec section 233400 "Fans " is a resource for high QUALITY fan/drive spec. language.

* + - 1. Fan and Motor:
         1. Fan: Galvanized steel or aluminum wheels; galvanized-steel fan scrolls. Adjustable speed belt drive with motor mounted on an adjustable steel base plate.
         2. Motor: Provide motors in compliance with Related Section "Motors".
         3. Motor Wiring: Terminate wiring in a junction box, external to the unit casing.
      2. SOURCE QUALITY CONTROL
         1. Factory test all coils with a minimum of 350 psig air pressure while submerged under water.
         2. Assemble and factory test each unit prior to shipping. Cycle controls and operate fan at all speeds to check for proper operation. Correct all deficiencies prior to shipping.
    1. EXECUTION
       1. EXAMINATION AND PREPARATION
          1. Examine areas to receive blower-coil units for compliance with requirements for installation tolerances and other conditions affecting performance.
          2. Examine rough-in construction for piping and electrical connections to verify actual locations before blower-coil-unit installation.
          3. Proceed with installation only after unsatisfactory conditions have been corrected.
       2. INSTALLATION
          1. Install blower coil units level and plumb and to comply with Quality Assurance Standards and manufacturer’s installation instructions.

Regarding the below paragraph: Be sure to show overflow drain routed to a CONSPICUOUS termination point, if an OVERFLOW drain is being used.

* + - 1. CONNECTIONS
         1. General piping installation requirements are specified in other Related Documents Specification Sections. Drawings indicate general arrangement of piping, fittings, and specialties. Connect hydronic, condensate drain, and overflow drain piping to the unit.
      2. TEMPORARY USE PRIOR TO OCCUPANCY
         1. Start units for temporary use only with the express written permission of the Owner and compliance with all requirements of the Contract Documents.
         2. Complete all drywall taping, sanding and finishing in an area prior to any early use of units serving that area.
         3. Thoroughly clean unit of all grease, dirt, dust, etc.
         4. Prior to placement into temporary service:

Perform manufacturer’s pre-start protocol.

Perform commissioning activities.

* + - * 1. Install a complete set of temporary filters in the unit equal to the quality and efficiency of the specified permanent filters. If the unit was equipped with pre-installed filters, they may be used for temporary service. Provide factory new, clean filters in units at final turn over to the Owner.
        2. During temporary service, perform all manufacturer’s recommended and required routine maintenance procedures, including filter replacement at regular intervals, as required. Continuously maintain a log of all such procedures completed. Store log at unit during temporary use period and include log as part of the final Operation and Maintenance Manual.
      1. FIELD QUALITY CONTROL
         1. Perform the following field tests and inspections and prepare test reports:

Test and adjust controls and safety devices. Replace damaged and malfunctioning controls and equipment.

Test unit operation with thermostat in all modes of operation.

Verify that drain pans collect all condensate and are properly sloped to drain so that no condensate is retained in the pans.

Remove and replace malfunctioning units and retest as specified above.

* + - 1. Commissioning
         1. Perform the commissioning activities as outlined in the Division 1 Section titled Commissioning and other requirements of the Contract Documents.
      2. CLOSEOUT ACTIVITIES
         1. Perform all commissioning activities, even if previously performed to ready for temporary use.
         2. After unit has completed final commissioning and just prior to final acceptance by Owner:

Thoroughly clean unit of all grease, dirt, dust, etc., lubricate bearings, align and tighten belts.

Install a new, complete set of filters.

Touch up damaged galvanized surfaces with zinc rich paint, minimum 65 percent metallic zinc by weight. Touch up damaged painted surfaces with manufacturer provided touch-up paint

* + - 1. OWNER TRAINING
         1. In cooperation with the Commissioning Agent, train Owner’s personnel on basic blower-coil unit maintenance by demonstrating the following: location of control devices, removal of access panels, filter replacement, and motor replacement.

END OF SECTION 238221