FUNCTIONAL TEST AIR HANDLER-6

University of Michigan Plant Extension

Commissioning and Plan Review Department

Phone (734) 615-7168 Fax (734) 936-3334

This is not a punch list.  The engineer of record, not the commissioning team, performs Punch listing.

Project Name: XXX					Project Number: XXXX-XX-XXX

Tag No.			Model No.			Serial No.

Attendees:

1) _________________________________________ 2)____________________________________

3) _________________________________________ 4)____________________________________

5) _________________________________________ 6)____________________________________

7) _________________________________________ 8)____________________________________

Is system operating or is this initial start-up? _________________________________________________

Is the Pre-Start Checklist Complete? _______________________________________________________

# Fan

_______ Is there any drag when fan is hand rotated?

_______ Fan has correct rotation

_______ Drive belt tension correct

_______ Is there any unusual vibration? (Check throughout fan range if variable speed)

_______ Is there any unusual noise?

_______ Is there any casing leakage?

_______ Is there any motor over-heating?

_______ Back draft dampers open and close smoothly

_______ Do the control dampers function?

Belt tension checked after 8 hours of operation

Belt tension checked after 24 hours of operation

Belt tension checked after 100 hours of operation

Max allowable fan RPM:  _______	     Design fan RPM:  _______  	Measured fan RPM:  _______

Design amp draw (L1/L2/L3):       ______ / _______ / ________

Measured amp draw (L1/L2/L3):  ______ / _______ / ________

Design voltage (L1/L2/L3):      ______ / _______ / ________

Measured voltage (L1/L2/L3): ______ / _______ / ________

Controls

______HOA switches and lights work: _____________________________________________________

______Alarms activate locally: ____________________________________________________________

______Alarms activate via DDC: __________________________________________________________

______Fans will start/stop/change speed via DDC_____________________________________________

Remarks:

DDC Control Remarks:

## Completed by (print): 				 	Company:

Signed: 						 	Date:

Witnessed By:						Date:

U of M Commisioner