CHECK-TEST-START-UP/FUNCTIONAL TEST

University of Michigan

Facilities Evaluation and Commissioning Dept.

Phone (734) 615-7168  Fax (734) 936-3334

Emergency Generators/Auto Transfer Switches

Notice: This is not a punch list.  Check-off indicates system is in general compliance, was readied for functional testing, and was tested.  Punch listing is performed by the engineer of record, not the commissioning team.

Project Name:

Project Number

Start-up Date:

Attendees/Representing:

1) _________________________________________     2)____________________________________

3) _________________________________________     4)____________________________________

5) _________________________________________     6)____________________________________

7) _________________________________________     8)____________________________________

Generator Mfg/Size:_________________________Model: ______________________

Location: __________________________Prime Mover________________________

Fuel:___________  Radiator (describe): _____________________________________

Major Accessories: _________________________________________________________________

_____________________________________________________________________________________

_____________________________________________________________________________________

Purpose: _______________________________________________________________

Is system operating or is this initial start-up?__________________________________________________

_____________________________________________________________________________________

Note: Indicate N/A where not applicable

Prestart Checks/Tests

Cooling System

_______  motorized exhaust louver _______  motorized supply louver  _________ Duct flex connectors

_______  Supply air and exhaust air system correctly installed for this generator

Fuel Train

_______  Correct fuel supply _________Required fuel pressure_________ Actual (unit off) fuel pressure

_______  Fuel filter/strainer installed  ________  Fuel line solenoid (gas units) checked

Prime Mover

_______  50/50 EG coolant?  _________  Coolant level checked

_______  Prime mover oil level _________Govenor oil level

_______  Air cleaner in place and clean _________ Belts properly tightened

_______  Power take-off bearings lubricated

_______  Block heater checked

_______  Radiator fan free to rotate  _______  Fan bearings lubricated

_______  No leaks: fuel, coolant, oil

_______  Idle speed checked/adjusted

_______  Idle mixture checked/adjusted

_______  Ignition timing checked/adjusted

_______  Throttle and govenor checked/adjusted

_______  PTO clutch release and shaft bearings checked/adjusted

_______  Battery electrolyte level checked _________ Battery cables tight________ Battery clamped tight

_______  Battery charger set up and functions properly

_______ Charger not located above or below battery (fumes or dripping acid will corrode)

_______  Isolators free floating and level

_______  Exhaust flex connector   _________ Exh. rain cap _________ Exh. pipe is Sch. 40 steel pipe

_______  Exh. water trap before silencer, w/drainage plug or petcock

Generator and Auto Transfer Switch

_______  Generator oil level

_______  All control panel functions tested  _________  Controller accessible

_______  All remote annunciator panel functions tested  _________ annunciator accessible

_______  Transfer switch control panel functions tested  _________ ATS accessible

_______  generator strip heater  ________  Controller strip heater

Crank setting: cyclic or continuous? ___________________________________________________

Misc. Installation

_______  All fasteners tight

_______  No rigid conduit connections

_______  No rigid fuel line connections

_______  No data plate damage/data plate legible

_______  Generator set properly anchored to base (note- normally expansion anchors are not permitted by

the genset mfg….. anchor bolts are to be poured into concrete)

_______  No blockage of air flow around unit  _______ Unit has been cleaned up

ATS Settings:

__________ ATS outage time delay  __________  Transfer to emergency time delay

__________  Re-transfer to normal time delay __________ Generator "off delay

Comments______________________________________________________________________

_______________________________________________________________________________

_______________________________________________________________________________

_______________________________________________________________________________

_______________________________________________________________________________

_______________________________________________________________________________

_______________________________________________________________________________

_______________________________________________________________________________

_______________________________________________________________________________

_______________________________________________________________________________

_______________________________________________________________________________

_______________________________________________________________________________

_______________________________________________________________________________

Operational Test:

Turn gas fired equipment on same gas lead "on".  Open normal power breaker:

_______  ATS transfers load to generator

_______  Motorized exhaust louver cycles open

_______  Generator starts, emergency lighting and exit signs to full brilliance within 10 seconds

_______  Remote enunciator signals generator "on".

_______  Generator running w/o problems

_______  Restore normal power.  ATS transfers to normal.  Generator shutdown after time delay.

_______  Fuel solenoid closes

_______  Remote enunciator signals generator "off".

_______  Successful second cycle of above tests.

_______  Successful third cycle of above tests.  For third cycle, generator to run under load for 30 minutes

w/o problems.

Third cycle data: (collected from control panel metering… take near end of 30 minute cycle)

Load Amps ______/______/______  Load Volts  ______/______/______ Load Hz  ______/______/_____

Calculated KVA ________________________________________________________________________

Battery volts _______  Engine water temp  ________ Engine oil pressure ________

Additional Tests:

Verify Generator Control Panel Functions:

_______ Cool down timer  ________ System ready lamp  ________ System not in auto lamp

_______  Alarm horn/silence  _________  Lamp test switch  _________Hour meter

_______  Run/off/reset – auto switch  _______ Emergency stop switch

Verify ATS Control Panel Functions:

_______ Load Normal Pilot  ________ Load Emergency Pilot

_______ Source Normal Pilot  ________ Source Emergency Pilot

_______ Transfer switch test  _________ Bypass time delay switch test  _______ Engine exerciser switch

Comments______________________________________________________________________

_______________________________________________________________________________

_______________________________________________________________________________

_______________________________________________________________________________

_______________________________________________________________________________

_______________________________________________________________________________

_______________________________________________________________________________

_______________________________________________________________________________

_______________________________________________________________________________

I certify all the required pre-start checks required by the manufacturer and listed above were done, all information noted above is correct, and this equipment is adjusted and operates properly:

Print Name: __________________________________ Representing __________________________

Signed:____________________________________________________________________________