FUNCTIONAL TEST - GENERATOR

University of Michigan Plant Extension

Commissioning and Plan Review Department

Phone (734) 615-7168 Fax (734) 936-3334

This is not a punch list.  The engineer of record, not the commissioning team, performs Punch listing.

Project Name: XXX					Project Number: XXXX-XX-XXX

Tag No.			Model No.			Serial No.

Attendees:

1) _________________________________________ 2)____________________________________

3) _________________________________________ 4)____________________________________

5) _________________________________________ 6)____________________________________

7) _________________________________________ 8)____________________________________

9) _________________________________________ 10)___________________________________

11) ________________________________________ 12)___________________________________

Check     Item							Comments

General

Is system operating or is this initial start-up?

Is the Pre-Start Checklist Complete?

Generator Mfg/Size:

Cooling System

Motorized exhaust & supply louver

Duct flex connectors

Supply air and exhaust air system correctly installed for this generator

Fuel Train

Fuel type

Required fuel pressure

Actual (unit off) fuel pressure

Fuel line solenoid (gas units) checked

Prime Mover

Coolant level checked

Prime mover oil level full

Air cleaner in place and clean

Belts properly tightened

Power take-off bearings lubricated

Block heater checked

Fan bearings lubricated

No leaks: fuel, coolant, oil, etc.

PTO clutch release and shaft bearings checked/adjusted

Isolators free floating and level

Exhaust flex-connector installed

Exhaust rain cap installed

Exhaust water trap before silencer, w/drainage plug or petcock

Crank setting cyclic or continuous?

Battery System

Electrolyte level checked

Battery cables tight

Battery clamped tight

Battery charger set up and functions properly

Charger not located above or below battery (fumes or dripping acid will corrode)

Generator and Auto Transfer Switch

Generator oil level checked

All control panel functions tested

All remote annunciator panel functions tested

Transfer switch control panel functions tested

All fasteners tight

No rigid conduit connections

No rigid fuel line connections

Data nameplate legible

Generator set properly anchored to base

(note- normally expansion anchors are not permitted by the mfg… anchor bolts are to be poured into concrete)

No blockage of air flow around unit

Unit has been cleaned up

ATS Settings:

Outage time delay

Transfer to emergency time delay

Re-transfer to normal time delay

Generator off delay

Operational Test:

(Turn gas fired equipment on and open normal power breaker)

ATS transfers load to generator

Motorized exhaust louver cycles open

Generator starts, emergency load picked-up within 10 seconds

Remote annunciator signals generator "on".

Generator running w/o problems

(Restore normal power breaker)

ATS transfers to normal

Generator shutdown after time delay

Remote annunciator signals generator "off"

Successful second cycle of above tests

Successful third cycle of above tests

(For third cycle, generator to run under 80% full load for 120 minutes minimum w/o problems)

Third cycle data: (collected from control panel metering… take near end of 120 minute cycle)

Amp draw (A/B/C): _____ / _____ / _____

Voltage (AB/BC/AC): _____ / _____ / _____

Frequency (Hz):

Battery volts

Engine water temp

Engine oil pressure

Additional Tests:

Verify Generator Control Panel Functions:

Cool down timer

System ready lamp

System not in auto lamp

Alarm horn/silence

Lamp test switch

Hour meter

Run/off/reset – auto switch

Emergency stop switch

Engine Overspeed

Verify ATS Control Panel Functions:

Load Normal Pilot

Load Emergency Pilot

Source Normal Pilot

Source Emergency Pilot

Remarks:

Completed by (print): __________________________ Company: ______________________________

Signed: _______________________________________ Date: _________________________________