Pre-Start Check List

University of Michigan

Facilities Evaluation and Commissioning Dept.

Phone: (734) 615-7168   Fax: 936-3334

This document shall be filled out by the contractor and provided to the UM Commissioning Engineer in advance of actual equipment start-up.  Note "NA" for not applicable, "NO" for problem or non-compliance .  This document is to be used in conjunction with the manufacturer's pre-start check list.

Project Name:

Project Number:

Completed by/representing (print):

# Gas Fired Atmospheric Steam Generator/ Humidifier

Tag No. 			Model No. 				Serial No.

Check		Item					Comments

General Requirements

Equipment and components match reviewed and approved shop drawings

Installation instructions and drawings were reviewed during installation

Equipment and components are free of obvious physical damage

Equipment and surrounding area is clean

Nameplate data has been recorded, nameplate is attached and legible

Manufacturer's pre-start requirements have been reviewed and completed

Coordination - the following must be notified of humidifier start-up and be in attendance

Mechanical Contractor

Controls contractor

Manufacturer's representative.

U of M DDC technician

U of M commissioner

Start-up will be conducted by:

Installation Requirements

All piping is properly supported and insulated

AHU,  CW,  Drain,  Power and controls ready for operation

Steam Generator is set in place

Properly supported

Accessible for service

Humidifier(s) are installed in duct and ready

Properly attached and supported

Accessible for service. Duct access door installed.

Proper material used for downstream duct,  per specification

Nozzles pointing in proper direction

Cold Water piping complete and ready

Water softener/ RO System is complete, started, regenerated

Piping installed per detail and manufacturer's instructions

Piping is flushed up to steam generator inlet

# Gas Fired Atmospheric Steam Generator/ Humidifier Pre-Start Checklist

Steam piping complete and ready

Proper material used for piping,  per specification and manufacturer

Piping installed per detail and manufacturer's instructions

Piping pitches continuously back to steam generator

Piping includes no valves or restrictions

Condensate/ Drain piping complete and ready

Proper material used for piping,  per specification and manufacturer

Piping installed per detail and manufacturer's instructions

Piping pitches continuously to cooling basin

Piping includes trap,  means of priming,  and is primed

Cooling basin and valve is installed

Gas piping complete and ready

Piping installed per detail and manufacturer's instructions

Record inlet gas pressure

Exhaust stack complete and ready

Stack installed per detail and manufacturer's instructions

Stack penetrates roof safely and terminates per code requirements

Power wiring complete and ready

Cord from unit reaches 120V outlet

Power hard wired to unit with local disconnecting means.

Control are complete and ready

High limits installed,  wired,  ready

DDC I/O terminated at steam generator and DDC panel

DDC panel ready to generate/ receive DDC I/O

Additional requirements have been completed

Additional Comments:

Certification:  I certify the above checks have been made and unit is ready for start-up  (signed/date)