Pre-Start Check List

University of Michigan

Facilities Evaluation and Commissioning Dept.

Phone: (734) 615-7168   Fax: 936-3334

This document shall be filled out by the contractor and provided to the UM Commissioning Engineer in advance of actual equipment start-up.  Note "NA" for not applicable, "NO" for problem or non-compliance.  This document is to be used in conjunction with the manufacturer's pre-start checklist.

Project Name:

Project Number:

Completed by/representing (print):

# Pumps

Tag No. 			Model No. 				Serial No.

Check		Item					Comments

General

Flushing complete, strainers cleaned:

Construction strainer element in place

Inertia base vibration isolators (aligned, weight even distributed, free floating)

Preliminary pump alignment complete

Pump hung correctly

Grouted

No grout shrinkage indicating wrong grout or concrete used

Grout extends under channel base

Channel base supported on wedges

Pump off/rotate by hand/no drag

Pump data label secure, legible and undamaged.

Pump data label info matches approved submittal

No pipe weight or torque on pump flanges

Pipe connections to pump not sprung in place

Flexible connection not torqued/mis-aligned

Flexible connection flange bolts not contacting rubber sphere

5 Dia. straight inlet pipe or suction diffuser

Gages positioned to be readable

Gage scale ranges reasonable

Pipe Hangers-

Correct type

Correct installation

Vapor barrier integrity (no tears, punctures, gaps, lagging lapped onto insul shields, etc.)

Spring Isolator Hangers-

Correct type

Correct location

Spring on bottom, rubber on top

Housing can fully rotate without contacting adjacent obstructions

No sort circuits

Certification:  I certify the above checks have been made (signed/date)