Editors Note: Blue text not to be changed.  Remember to fill in system name in title and footer.

PRE-START CHECKLIST- SUBSTATION

University of Michigan Plant Extension

Commissioning & Plan Review Department

Phone (734) 615-7168  Fax (734) 936-3334

This document shall be filled out by the contractor and provided to the UM Commissioning Engineer at least 7 days in advance of the actual equipment start-up. Note “NA” for not applicable or “NO” for problem or non-compliance. This document is to be used in conjunction with the manufacturer’s pre-start checklist.

Project Name: XXX			 		Project Number: XXXX-XX-XXX

Tag No.			Model No.			Serial No.

Check     Item							Comments

General Data:

___ Transformer nameplate data is complete, legible, and on front of equipment ______________________

___ kVA (record):  ___________________________________________________________________

___ Voltage primary & secondary (record): ________________________________________________

___ Degrees Rise (record): _____________________________________________________________

___ Impedance (record): _______________________________________________________________

___ Taps 1+ and 3- (record): ___________________________________________________________

___ Substation complies with approved shop drawings ___________________________________________

___ Assembly is complete and front aligned ___________________________________________________

___ Electrical testing is complete ____________________________________________________________

___ Independent testing agency reports turned over to Commissioner for review ___________________

___ All connections are torqued to manufacturer recommendation __________________________________

___ Key interlocks installed and operational ___________________________________________________

___ Proper clearance is obtained ____________________________________________________________

___ 5'-0" minimum front and back and 6'-6" AFF minimum (over 600V) _________________________

___ 3'-6" minimum front and back and 6'-6" AFF minimum (600V & below) _____________________

___ Equipment room is clean, protected from dust, and securable __________________________________

___ Painting/finishings complete or shutdown scheduled to complete ___________________________

___ Substation room accessible by authorized personnel only (UM High Voltage has key) ___________

___ Doors have crash-bar hardware installed _______________________________________________

___ Permanent or temporary high voltage warning signage installed_________________________________

Housekeeping Pad:

___ Housekeeping pad is proper height ______________________________________________________

___ Leveling channels installed ____________________________________________________________

___ Equipment is anchored _______________________________________________________________

Primary:

___ Cables are installed and terminated _____________________________________________________

___ Phasing is correct ___________________________________________________________________

___ Transformer disconnect settings (record): ________________________________________________

Secondary:

___ Breakers are installed and rack in and out smoothly ________________________________________

___ Phasing is correct ___________________________________________________________________

___ Breaker lift installed and operable ______________________________________________________

___ Breaker labels installed and correctly identified ___________________________________________

___ Service disconnect settings (record): ____________________________________________________

Start-Up:

___ Start-up scheduled for: ____________________,  to be conducted by:_________________________

___ Start-up notification faxed to UM commissioner 7 days in advance of scheduled start-up.

___ Metering Calibrated _________________________________________________________________

Remarks:____________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________

## Completed by (print): ___________________________Company: _________________________

Signed: ____________________________________________Date:________________________________